# HOT WORK PERMIT

[Seek an alternative method using Decision Tree wherever possible]

Before initiating any Hot Work, ensure precautions are in place as required by NFPA51B& ANSI Z49.1. Make sure appropriate Fire Extinguisher is readily available.

This Hot Work Permit is required for any operation involving open flames or producing heat and or sparks. This work includes, but is not limited to welding, brazing, cutting, grinding, soldering, thawing pipe, torch-applied roofing or chemical welding.

| Date | Hot Work by Employee Contractor |
| --- | --- |
| Location / Building & floor | Name & Signature of the Person doing Hot Work |
| Work to be done | I verify the above location has been examined, the precautions marked on the checklist below have been taken, and permission is granted for this work. Name and Signature of the Permit-Authorizing Individual (PAI) |
| Time Stated Time completed THIS PERMIT IS FOR ONE (1) DAY ONLY |  |
| - Available sprinklers, hose streams and extinguishers are in service and operable. |  |
| - Hot Work equipment is in good condition in accordance with Manufacturer’s specification. |  |
| - Special permission is obtained to conduct hot work on metal vessels or piping lined with rubber or plastic. |  |
| Requirements within 35 ft (11 m) of Hot Work - Flammable liquid, dust, lint, and oily deposits removed. - Explosive atmosphere in area eliminated. - Floor swept clean and trash removed. - Combustible floors wet down or covered with damp sand or fire-resistive/non-combustible materials or equivalent. - Personal protection from electrical shock when floors are wet. - Other combustible storage materials removed or covered with listed or approved materials (welding pads, blankets, or curtains; fire-resistive tarpaulins), metal shields or non-combustible materials. - All wall and floor openings covered. - Ducts and conveyors that might carry sparks to distant combustible material covered, protected or shut down. |  |
| Requirements for Hot Works on walls, ceilings or roofs - Construction is non-combustible and without combustible coverings or insulation. - Combustible materials on other side of walls or ceilings or roofs are moved away. |  |
| Requirements for Hot Works on enclosed equipment - Enclosed equipment is cleaned of all combustibles. - Containers are purged of flammable liquid / vapor. - Pressurized vessels, piping and equipment removed from service, isolated and vented. |  |
| Requirement for Hot Work fire watch and fire monitoring - Fire watch is provided during and for a minimum of 30 minutes after hot work, including any break activity. - Fire watch is provided with suitable extinguishers and where, practical, charged small hose. - Fire watch is trained in use of equipment and in sounding alarm. - Fire watch can be required in adjoining areas, above and below: - Yes  No Per the PAI / Fire Watch monitoring of hot work area has been extended beyond the 30 minute. |  |